## Ranking
MS4 Outfall | Receiving Water | Segment ID | Priority | Rank End of Permit Year 3 | Date of Dry Weather Screening | Testing Company | Weather | Outfall Located | Outfall Material | Outfall Size (Inches) | Outfall Condition | Needs Cleaning | Needs Repair | Weather (Dry/Wet) | Precipitation, Antecedent 24 hours | Standing Water | Standing Water Color | Sampling Location | If MH, ID | Sample Taken | If no, why | Flow | Velocity | Flow Color | Depth of Flow (Inches) | Sediment | Sediment (%) | Floatables | Odor | pH | Temperature (⁰C) | Specific Conductivity (µs/cm) | Salinity (µg/L or ppt) | Ammonia (mg/L) | Surfactants (mg/L) | Chlorine (mg/L) | E. Coli (MPN/100mL) | Meets Likely Sewer Indicators? (Yes/No) | BOD5 (mg/L) | Dissolved Oxygen (mg/L) | Total Suspended Solids (TSS) (mg/L) | Phosphorus (Total) (mg/L) | Phosphorus (Total) (µg/L) | Total Lead (mg/L) | Total Arsenic (mg/L) | Total Copper (mg/L) | Oil and Grease (mg/L) | Fecal Coliform (CFU/100mL) | Comments
31 (Interconnection with City of Medford) | Mystic River | MA71-02 | Problem | 1 | 2020-10-15 | SDE, Inc. | Sunny | Yes | Reinforced Concrete | 48 | Good | No | No | Dry | <0.1 | No |  | Manhole | 31-5008 | Yes |  | Yes | Slow | Clear | 1 | No |  | None | None | 7.23 | 20 | 1475 | 0.7 | 5 | 0.25 | 0.06 | 24196 | Yes | <3.0 | 3.01 | 9.7 | 0.3 | 300 | n/a | <0.05 | n/a | n/a | n/a | Construction in area of interconnection.
25 | Mystic River | MA71-02 | Problem | 2 | 2020-10-15 | SDE, Inc. | Sunny | Yes | Reinforced Concrete | 60 | Good | No | No | Dry | <0.1 | No |  | Outfall |  | Yes |  | Yes | Medium | Yellow | 0.2 | Yes | 5 | Oily Sheen | None | 7.95 | 17 | 6300 | 3.4 | 2 | 1 | 0.17 | 63 | Yes | <10 | 5.53 | 28 | 0.03 | 30 | n/a | <0.05 | n/a | n/a | n/a
28 | Mystic River | MA71-02 | Problem | 3 | 2020-10-15 | SDE, Inc. | Sunny | Yes | Cast Iron | 16 | Good | No | No | Dry | <0.1 | No |  | Outfall |  | Yes |  | Yes | Medium | Clear | 0.1 | Yes | 10 | None | None | 7.05 | 17 | 2680 | 1.4 | 2 | 0.5 | 0.17 | 10 | Yes | <3.0 | 3.96 | 18 | 0.12 | 120 | n/a | <0.05 | n/a | n/a | n/a
10 | Alewife Brook | MA71-04 | High | 4 | 2020-10-15 | SDE, Inc. | Sunny | Yes | Reinforced Concrete | 36 | Good | No | No | Dry | <0.1 | No |  | Outfall |  | Yes |  | Yes | Slow | Clear | 0.1 | No |  | None | None | 8.21 | 18 | 688 | 0.3 | 0.1 | 0 | 0.06 | 8164 | No | <3.0 | 8.14 | 9 | 0.11 | 110 | <0.025 | n/a | <0.025 | = <0.5 | n/a
8 | Alewife Brook | MA71-04 | High | 5 | 2020-10-15 | SDE, Inc. | Sunny | Yes | Cement Concrete | 24 | Good | No | No | Dry | <0.1 | No |  | Outfall |  | Yes |  | Yes | Medium | Clear | 0.5 | No |  | None | None | 8.06 | 16 | 2 | 1 | 0.1 | 0.5 | 0 | 4106 | No | <3.0 | 7.92 | 4.7 | 0.05 | 50 | <0.025 | n/a | <0.025 | 2 | n/a
7 | Alewife Brook | MA71-04 | High | 6 | 2020-10-15 | SDE, Inc. | Sunny | Yes | Reinforced Concrete | 24 | Good | No | No | Dry | <0.1 | No |  | Outfall |  | Yes |  | Yes | Medium | Clear | 0.5 | No |  | None | None | 8.02 | 17 | 1772 | 0.9 | 0 | 0.25 | 0.11 | 1607 | No | <3.0 | 8.01 | 3.7 | 0.08 | 80 | <0.025 | n/a | <0.025 | 0.6 | n/a
11 | Alewife Brook | MA71-04 | High | 7 | 2020-10-15 | SDE, Inc. | Sunny | Yes | Cement Concrete | 12 | Good | No | No | Dry | <0.1 | No |  | Outfall |  | Yes |  | Yes | Slow | Clear | 0.5 | No |  | None | Musty | 6.97 | 20 | 393 | 0.2 | 0 | 0.25 | 0 | 985 | No | <3.0 | 5.79 | 16 | 0.09 | 90 | <0.025 | n/a | <0.025 | = <0.5 | n/a
29 | Mystic River | MA71-02 | High | 8 | 2020-10-15 | SDE, Inc. | Sunny | Yes | Reinforced Concrete | 32 | Good | No | No | Dry | <0.1 | No |  | Outfall |  | Yes |  | Yes | Medium | Clear | 0.1 | No |  | None | None | 8 | 16 | 1436 | 0.7 | 0.1 | 0.5 | 0.16 | 246 | No | <3.0 | 6.38 | 13 | 0.1 | 100 | n/a | <0.05 | n/a | n/a | n/a
32 | Mystic River | MA71-03 | High | 9 | 2020-10-16 | SDE, Inc. | Partly Cloudy | No | Unknown | Unknown |  |  |  | Dry | <0.1 | No |  | Manhole | 32-6334 | Yes |  | Yes | Slow | Clear | 6 | No |  | None | Musty | 6.99 | 20 | 3570 | 1.8 | 5 | 1.5 | 0 | 20 | No | <8.0 | 2.67 | n/a | 0.23 | 230 | n/a | n/a | n/a | 1.4 | 70 | Iron deposits.
19 | Mystic River | MA71-02 | High | 10 | 2020-10-15 | SDE, Inc. | Sunny | Yes | Reinforced Concrete | 60 | Good | No | No | Dry | <0.1 | No |  | Outfall |  | Yes |  | Yes | Medium | Clear | 0.1 | No |  | None | None | 8.59 | 19 | 1846 | 0.9 | 0.1 | 0 | 0.04 | 168 | No | <3.0 | 6.48 | 8.3 | 0.11 | 110 | n/a | <0.05 | n/a | n/a | n/a
21 | Mystic River | MA71-02 | High | 11 | 2020-10-15 | SDE, Inc. | Sunny | Yes | Reinforced Concrete | 60 | Good | No | No | Dry | <0.1 | No |  | Outfall |  | Yes |  | Yes | Medium | Clear | 0.1 | No |  | None | None | 8.38 | 19 | 1681 | 0.8 | 0 | 0 | 0.16 | 10 | No | <3.0 | 6.45 | 3.3 | <0.02 | Below Detection Limit | n/a | <0.05 | n/a | n/a | n/a
26 * | Mystic River | MA71-02 | High | 12 | 2020-10-15 | SDE, Inc. | Sunny | Yes | Cured In Place | 8 | Good | No | No | Dry | <0.1 | No |  | Outfall |  | No | Dry | No |  |  |  | No |  | None | None | [8 empty] | No
4 | Alewife Brook | MA71-04 | High | 13 | 2020-10-16 | SDE, Inc. | Partly Cloudy | Yes | Vitrified Clay | 18 | Good | No | No | Dry | <0.1 | No |  | Outfall |  | No | Dry | No |  |  |  | No |  | None | None | [8 empty] | No
12 | Mystic River | MA71-02 | High | 14 | 2020-11-04 | SDE, Inc. | Sunny | Yes | Cement Concrete | 18 | Good | No | No | Dry | <0.1 | No |  | Outfall |  | No | Dry | No |  |  |  | No |  | None | None | [8 empty] | No
9 | Alewife Brook | MA71-04 | High | 15 | 2020-10-15 | SDE, Inc. | Sunny | Yes | Cement Concrete | 30 | Good | No | No | Dry | <0.1 | No |  | Outfall |  | No | Dry | No |  |  |  | No |  | None | None | [8 empty] | No
6 | Alewife Brook | MA71-04 | High | 16 | 2020-10-15 | SDE, Inc. | Sunny | Yes | Reinforced Concrete | 12 | Good | No | No | Dry | <0.1 | No |  | Outfall |  | No | Dry | No |  |  |  | No |  | None | None | [8 empty] | No
Notes:
n/a | indicates the parameter was not a pollutant of concern at the outfall where the sample was taken.
* | Screened at the DCR outfall during Permit Year 3. Correct City outfall 26 has been identified and screened in July 2021 (Permit Year 4). This table shows the results of the screening during Permit Year 3 at the DCR outfall.